## Ordered Measurements
Measurements
Order | Setup | Failure description | Severity | Speed (%) | Speed (RPM) +- 5 | Pressure (bar) +- 0.1 | Flow (m3/h) +- 5 | Alignment report | Comments
1 | motor 4 | Healthy 1 | N/A | 70% | 2070 | 1.1 | 85 | 1 | Initial flow measurements inconsistent with remaining measurements.
2 | motor 4 | Align angular | 1 | 70% | 2070 | 1.1 | 95 | 2 | 0.1/100 mm. Initial flow measurements inconsistent with remaining measurements.
3 | motor 4 | Align angular | 2 | 70% | 2070 | 1.1 | 125 | 3 | 0.2/100 mm
4 | motor 4 | Align angular | 3 | 70% | 2070 | 1.1 | 125 | 4 | 0.3/100 mm
5 | motor 4 | Align angular | 4 | 70% | 2070 | 1.1 | 125 | 5 | 0.5/100 mm
6 | motor 4 | Align angular | 5 | 70% | 2070 | 1.1 | 125 | 6 | 1.1/100
7 | motor 4 | Align parallel | 1 | 70% | 2070 | 1.1 | 120 | 7 | 0.1 mm
8 | motor 4 | Align parallel | 2 | 70% | 2070 | 1.1 | 120 | 8 | 0.2 mm
9 | motor 4 | Align parallel | 3 | 70% | 2070 | 1.1 | 120 | 9 | 0.5 mm
10 | motor 4 | Align parallel | 4 | 70% | 2070 | 1.1 | 120 | 10 | 1.0 mm
11 | motor 4 | Align combination | 4 | 70% | 2070 | 1.1 | 125 | 11 | 1.0/100 mm angular + 1.0 mm parallel
12 | motor 4 | Align combination | 3 | 70% | 2070 | 1.1 | 120 | 12 | 0.5/100 mm angular + 0.5 mm parallel
13 | motor 4 | Align combination | 2 | 70% | 2070 | 1.1 | 125 | 13 | 0.2/100 mm angular + 0.2 mm parallel
14 | motor 4 | Align combination | 1 | 70% | 2070 | 1.1 | 130 | 14 | 0.1/100 mm angular + 0.1 mm parallel
15 | motor 4 | Unbalance motor | 1 | 70% | 2070 | 1.1 | 125 | 15 | 5g motor side
16 | motor 4 | Unbalance motor | 2 | 70% | 2070 | 1.1 | 125 | 15 | 10g motor side
17 | motor 4 | Unbalance motor | 3 | 70% | 2070 | 1.1 | 125 | 15 | 20g motor side
18 | motor 4 | Unbalance motor | 4 | 70% | 2070 | 1.1 | 125 | 15 | 30g motor side
19 | motor 4 | Unbalance motor | 5 | 70% | 2070 | 1.1 | 125 | 15 | 80g motor side
20 | motor 4 | Unbalance motor | 6 | 70% | 2070 | 1.1 | 125 | 15 | 120g motor side
21 | motor 4 | Unbalance pump | 1 | 70% | 2070 | 1.1 | 125 | 15 | 30g pump side
22 | motor 4 | Unbalance pump | 2 | 70% | 2070 | 1.1 | 125 | 15 | 60g pump side
23 | motor 4 | Unbalance pump | 3 | 70% | 2070 | 1.1 | 125 | 15 | 90g pump side
24 | motor 4 | Coupling | 1 | 70% | 2070 | 1.1 | 125 | 15 | 1 sided cut block
25 | motor 4 | Coupling | 2D | 70% | 2070 | 1.1 | 125 | 15 | 2 sided cut block
26 | motor 4 | Coupling | 3 | 70% | 2070 | 1.1 | 125 | 15 | 1 block with low severity cut, 5 blocks with high severity cut
27 | motor 4 | Coupling | 2 | 70% | 2070 | 1.1 | 125 | 15 | 1 sided cut block, higher severity
28 | motor 4 | Cavitation suction | 1 | 70% | 2070 | 0.7 | 105 | 16 | Logical change in pressure and flow. Noticed small deviation in sound
29 | motor 4 | Cavitation suction | 2 | 70% | 2070 | 0.4 | 85 | 16 | Logical change in pressure and flow. No measurements for vibration due to file corruption.
30 | motor 4 | Cavitation suction | 3 | 70% | 2070 | 0.1 | 55 | 16 | Logical change in pressure and flow. Loud noise from pump
31 | motor 4 | Cavitation suction | 4 | 70% | 2085 | 0 | 25 | 16 | Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
32 | motor 4 | Cavitation discharge | 1 | 70% | 2075 | 1.3 | 90 | 16 | Quiet operation, Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
33 | motor 4 | Cavitation discharge | 2 | 70% | 2075 | 1.4 | 75 | 16 | Very quiet operation, Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
34 | motor 4 | Cavitation discharge | 3 | 70% | 2080 | 1.5 | 50 | 16 | Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
35 | motor 4 | Cavitation discharge | 4 | 70% | 2080 | 1.6 | 20 | 16 | Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
36 | motor 4 | Cavitation discharge | 5 | 70% | 2080 | 1.7 | 0 | 16 | Completely shut valve, Logical change in pressure and flow. higher rotational speed, probably due to less resistance of the impeller.
37 | motor 4 | Bent shaft | N/A | 70% | 2070 | 1.1 | 125 | N/A | No alignment report due to nature of the damage simulation
38 | motor 2 & 4 | Healthy noise | N/A | 100%/70% | 1480/2080 | 1,4/1,1 | 530 | 17 | Motor-pump setup 3 at 100% rated speed, Motor-pump setup 1 at 65% rated speed. Motor-pump setup 2 was running at 100% during this measurement. The flow is measured as the combined flow with all pumps running.
39 | motor 4 | Healthy 2 | N/A | 70% | 2070 | 1.1 | 120 | 17
40 | motor 4 | Healthy 3 | N/A | 70% | 2070 | 1.1 | 125 | 17
Order | Setup | Failure description | Severity | Speed (%) | Speed (RPM) | Pressure (bar) | Flow (m3/h) | Alignment report | Comments
1 | motor 2 | Healthy 1 | N/A | 100% | 1480 | 1.5 | 120 | 1 | All initial measured pressures seem slightly higher than later measurements. All initial measured flows are slightly lower than later measurements.
2 | motor 2 | Healthy 1 | N/A | 75% | 1110 | 0.8 | 100 | 1 | All initial measured pressures seem slightly higher than later measurements, this setting seems noisiest of the three speed settings, probably from valves discharge side of pump. Also resulting in a less stable measured pressure. All initial measured flows are slightly lower than later measurements.
3 | motor 2 | Healthy 1 | N/A | 50% | 740 | 0.2 | 65 | 1 | All initial measured pressures seem slightly higher than later measurements. All initial measured flows are slightly lower than later measurements.
4 | motor 2 | Impeller | 1 | 100% | 1480 | 1.4 | 120 | 2 | Balance report 1
5 | motor 2 | Impeller | 1 | 75% | 1110 | 0.8 | 100 | 2 | Balance report 1
6 | motor 2 | Impeller | 1 | 50% | 740 | 0.2 | 55 | 2 | Balance report 1
7 | motor 2 | Impeller | 2 | 100% | 1480 | 1.5 | 130 | 3 | Balance report 2
8 | motor 2 | Impeller | 2 | 75% | 1110 | 0.7 | 90 | 3 | Balance report 2
9 | motor 2 | Impeller | 2 | 50% | 740 | 0.2 | 45 | 3 | Balance report 2
10 | motor 2 | Impeller | 3 | 100% | 1480 | 1.4 | 135 | 4 | Balance report 3
11 | motor 2 | Impeller | 3 | 75% | 1110 | 0.8 | 105 | 4 | Balance report 3, seemingly less noise than previous cases.
12 | motor 2 | Impeller | 3 | 50% | 740 | 0.1 | 70 | 4 | Balance report 3
13 | motor 2 | Bearing BPFO | 1 | 100% | 1480 | 1.4 | 140 | 5 | Damage positioned in the loaded zone, directly underneath the shaft.
14 | motor 2 | Bearing BPFO | 1 | 75% | 1110 | 0.8 | 105 | 5 | Damage positioned in the loaded zone, directly underneath the shaft.
15 | motor 2 | Bearing BPFO | 1 | 50% | 740 | 0.1 | 75 | 5 | Damage positioned in the loaded zone, directly underneath the shaft.
16 | motor 2 | Bearing BPFO | 2 | 100% | 1480 | 1.4 | 140 | N/A | Damage positioned with the two lines equal distance from middle underneath the shaft. Alignment unchanged from BPFO 1, but no report.
17 | motor 2 | Bearing BPFO | 2 | 75% | 1110 | 0.7 | 105 | N/A | Damage positioned with the two lines equal distance from middle underneath the shaft. Alignment unchanged from BPFO 1, but no report.
18 | motor 2 | Bearing BPFO | 2 | 50% | 740 | 0.1 | 70 | N/A | Damage positioned with the two lines equal distance from middle underneath the shaft. Alignment unchanged from BPFO 1, but no report.
19 | motor 2 | Bearing BPFO | 3 | 100% | 1480 | 1.4 | 140 | 6 | Damage positioned with middle line directly underneath the shaft.
20 | motor 2 | Bearing BPFO | 3 | 75% | 1110 | 0.7 | 105 | 6 | Damage positioned with middle line directly underneath the shaft.
21 | motor 2 | Bearing BPFO | 3 | 50% | 740 | 0.1 | 70 | 6 | Damage positioned with middle line directly underneath the shaft.
22 | motor 2 | Bearing BPFI | 1 | 100% | 1480 | 1.4 | 140 | 7 | 1 damage line
23 | motor 2 | Bearing BPFI | 1 | 75% | 1110 | 0.8 | 105 | 7 | 1 damage line
24 | motor 2 | Bearing BPFI | 1 | 50% | 740 | 0.1 | 75 | 7 | 1 damage line
25 | motor 2 | Bearing BPFI | 2 | 100% | 1480 | 1.4 | 140 | 8 | 2 damage lines
26 | motor 2 | Bearing BPFI | 2 | 75% | 1110 | 0.8 | 105 | 8 | 2 damage lines
27 | motor 2 | Bearing BPFI | 2 | 50% | 740 | 0.1 | 70 | 8 | 2 damage lines
28 | motor 2 | Bearing BPFI | 3 | 100% | 1480 | 1.4 | 140 | 9 | 3 damage lines
29 | motor 2 | Bearing BPFI | 3 | 75% | 1110 | 0.7 | 105 | 9 | 3 damage lines
30 | motor 2 | Bearing BPFI | 3 | 50% | 740 | 0.1 | 70 | 9 | 3 damage lines. No measurement for vibration due to file corruption
31 | motor 2 | Bearing contaminated | N/A | 100% | 1480 | 1.4 | 140 | 10 | Running in for >30 minutes.
32 | motor 2 | Bearing contaminated | N/A | 75% | 1110 | 0.7 | 105 | 10
33 | motor 2 | Bearing contaminated | N/A | 50% | 740 | 0.1 | 70 | 10
34 | motor 2 | Bearing BSF | N/A | 100% | 1480 | 1.4 | 145 | 11 | slightly higher flow seems unrelated
35 | motor 2 | Bearing BSF | N/A | 75% | 1110 | 0.7 | 105 | 11
36 | motor 2 | Bearing BSF | N/A | 50% | 740 | 0.1 | 70 | 11
37 | motor 2 | Soft foot | 1 | 100% | 1480 | 1.4 | 140 | 12 | 0,5 double sided applied
38 | motor 2 | Soft foot | 1 | 75% | 1110 | 0.7 | 105 | 12 | 0,5 double sided applied
39 | motor 2 | Soft foot | 1 | 50% | 740 | 0.1 | 70 | 12 | 0,5 double sided applied
40 | motor 2 | Soft foot | 2 | 100% | 1480 | 1.4 | 140 | 13 | 1.0 double sided applied
41 | motor 2 | Soft foot | 2 | 75% | 1110 | 0.7 | 105 | 13 | 1.0 double sided applied
42 | motor 2 | Soft foot | 2 | 50% | 740 | 0.1 | 70 | 13 | 1.0 double sided applied
43 | motor 2 | Loose foot motor | N/A | 100% | 1480 | 1.4 | 140 | 14 | right driven-end foot
44 | motor 2 | Loose foot motor | N/A | 75% | 1110 | 0.7 | 105 | 14 | right driven-end foot
45 | motor 2 | Loose foot motor | N/A | 50% | 740 | 0.1 | 70 | 14 | right driven-end foot
46 | motor 2 | Loose foot pump | N/A | 100% | 1480 | 1.4 | 140 | 15 | left driven end foot
47 | motor 2 | Loose foot pump | N/A | 75% | 1110 | 0.7 | 105 | 15 | left driven end foot
48 | motor 2 | Loose foot pump | N/A | 50% | 740 | 0.1 | 70 | 15 | left driven end foot
49 | motor 2 | Broken rotor bar | N/A | 100% | 1480 | 1.4 | 140 | 16 | different motor
50 | motor 2 | Broken rotor bar | N/A | 75% | 1110 | 0.7 | 105 | 16 | different motor
51 | motor 2 | Broken rotor bar | N/A | 50% | 740 | 0.1 | 70 | 16 | different motor
52 | motor 2 | New motor | N/A | 100% | 1480 | 1.4 | 140 | 17 | same motor as used for stator short damage simulation, however, without any short applied.
53 | motor 2 | New motor | N/A | 75% | 1110 | 0.7 | 105 | 17 | same motor as used for stator short damage simulation, however, without any short applied.
54 | motor 2 | New motor | N/A | 50% | 740 | 0.1 | 70 | 17 | same motor as used for stator short damage simulation, however, without any short applied.
55 | motor 2 | Stator short | 1 | 100% | 1480 | 1.4 | 140 | 17 | approximately 25% short (analog dial)
56 | motor 2 | Stator short | 1 | 75% | 1110 | 0.7 | 105 | 17 | approximately 25% short (analog dial)
57 | motor 2 | Stator short | 1 | 50% | 740 | 0.1 | 70 | 17 | approximately 25% short (analog dial)
58 | motor 2 | Stator short | 2 | 100% | 1480 | 1.4 | 140 | 17 | approximately 50% short (analog dial), No measurements for current due to file corruption.
59 | motor 2 | Stator short | 2 | 75% | 1110 | 0.7 | 105 | 17 | approximately 50% short (analog dial)
60 | motor 2 | Stator short | 2 | 50% | 740 | 0.1 | 70 | 17 | approximately 50% short (analog dial)
61 | motor 2 | Healthy 2 | N/A | 100% | 1480 | 1.4 | 140 | 18
62 | motor 2 | Healthy 2 | N/A | 75% | 1110 | 0.7 | 105 | 18
63 | motor 2 | Healthy 2 | N/A | 50% | 740 | 0.1 | 70 | 18
64 | motor 2 & 4 | Healthy noise | N/A | 100%/70% | 1480/2080 | 1,4/1,1 | 530 | 18 | Motor-pump setup 3 at 100% rated speed, Motor-pump setup 1 at 65% rated speed. The flow is measured as the combined flow with all pumps running.
65 | motor 2 | Healthy noise | N/A | 75% | 1110 | 0.7 | 495 | 18 | Only motor 2 is measured, motor 4 is still on at 70%/2070 RPM and with 1,1 bar pressure.
66 | motor 2 | Healthy noise | N/A | 50% | 740 | 0.1 | 455 | 18 | Only motor 2 is measured, motor 4 is still on at 70%/2070 RPM and with 1,1 bar pressure.
67 | motor 2 | Healthy 3 | N/A | 100% | 1480 | 1.4 | 135 | 18
68 | motor 2 | Healthy 3 | N/A | 75% | 1110 | 0.7 | 100 | 18
69 | motor 2 | Healthy 3 | N/A | 50% | 740 | 0.1 | 70 | 18
70 | motor 2 | Bearing pump | 1 | 100% | 1480 | 1.4 | 140 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved
71 | motor 2 | Bearing pump | 1 | 75% | 1110 | 0.7 | 105 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved
72 | motor 2 | Bearing pump | 1 | 50% | 740 | 0.1 | 70 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved
73 | motor 2 | Bearing pump | 2 | 100% | 1480 | 1.4 | 140 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved
74 | motor 2 | Bearing pump | 2 | 75% | 1110 | 0.7 | 105 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved
75 | motor 2 | Bearing pump | 2 | 50% | 740 | 0.1 | 70 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved. Bearing at driven end replaced to rule out damage in the driven end bearing inner ring.
76 | motor 2 | Bearing pump | 3 | 100% | 1480 | 1.4 | 140 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved. Bearing at driven end replaced to rule out damage in the driven end bearing inner ring.
77 | motor 2 | Bearing pump | 3 | 75% | 1110 | 0.7 | 105 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved. Bearing at driven end replaced to rule out damage in the driven end bearing inner ring.
78 | motor 2 | Bearing pump | 3 | 50% | 740 | 0.1 | 70 | N/A | Noticed inner ring damage, alignment was validated, no alignment report saved. Bearing at driven end replaced to rule out damage in the driven end bearing inner ring.